## Series
Series
[5 empty] | d1* | d2 | h1 | [5 empty] | Copper | Tube
|  | Number of Lavatories | Pipe Size | Actual ID | Supply to first lavatory | between lavatories | height of lavatory supply | equivalent length of fittings | Total Developed Length | Flow | velocity | Pressure loss | Nominal | actual ID
|  | (qty) | (nominal) | (in) | (in) | (in) | (in) | (ft) | (ft) | (GPM) | (ft/sec) | (psi) | Size | (inches)
example drawn: |  | 3 | 0.75 | 0.785 | 33 | 30 | 6 | 5 | 15.25 | 6.5 | 4.3092 | 2.8395 | 0.5 | 0.545
|  | 3 | 0.75 | 0.785 | 33 | 30 | 6 | 5 | 15.25 | 6.5 | 4.3092 | 2.8395 | 0.75 | 0.785
|  | d1 is the length of pipe (horizontal) from larger supply pipe. | [9 empty] | User Input Cells
|  | If a riser is supplying the series, d1 is the distance to the riser. | [9 empty] | Calculated Values, Constants
|  | If a manifold or branch is supplying the series, d1 is the length of pipe to the manifold or branch. | [9 empty] | Important Values
Note on M4: Pressure loss from riser, branch, or manifold to most remote fixture.
Note on I6: EquivLength tab can be used to total equivalent length of fittings.
Note on I7: EquivLength tab can be used to total equivalent length of fittings.

## Ring
| Ring |  | The worst case pressure loss of a ring will be the fixture closest to the center of the total developed length. This sheet will help find the total developed length of the entire ring and calculate the pressure loss of half that distance. This will slightly overestimate the pressure loss.
[5 empty] | d1 | d2 | h1 | [5 empty] | Copper | Tube
|  | Number of Lavatories | Nominal Pipe Size | Actual ID | supply to first lavatory | distance between lavatories | height difference | Equivalent length of fittings | Total Developed Length of Ring | Flow | velocity | Pressure loss | Nominal | actual ID
|  | (qty) |  | (in) | (in) | (in) | (in) | (ft) | (ft) | (GPM) | (ft/sec) | (psi) | Size | (inches)
example drawn: |  | 3 | 0.75 | 0.785 | 24 | 30 | 6 | 6 | 23 | 6.5 | 4.3092 | 0.28157 | 0.5 | 0.545
|  | 3 | 0.75 | 0.785 | 24 | 30 | 6 | 6 | 23 | 6.5 | 4.3092 | 0.28157 | 0.75 | 0.785
|  | d1 is the length of pipe (horizontal) from larger supply pipe. | [9 empty] | User Input Cells
|  | If a riser is supplying the series, d1 is the distance to the riser. | [9 empty] | Calculated Values, Constants
|  | If a manifold or branch is supplying the series, d1 is the length of pipe to the manifold or branch. | [9 empty] | Important Values
Note on I6: EquivLength tab can be used to total equivalent length of fittings.
Note on I7: EquivLength tab can be used to total equivalent length of fittings.

## wsfuGPM (hidden)
demand
Load | tank | valve
| (GPM) | (GPM)
1 | 3 | 3 | note: zero fixtures allows the program to stop at one fixture unit. An input of zero is interpreted the same as blank.
2 | 3 | 3
3 | 5 | 5
4 | 6.5 | 6.5
5 | 8 | 8
6 | 9.4 | 15
7 | 10.7 | 17.4
8 | 11.8 | 19.8 |  |  | 0.5 | 0.75 | 1 | 1.25 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4
9 | 12.8 | 22.2 |  | 90 deg elbow | 1 | 1.5 | 2.5 | 3 | 4 | 5.5 | 7 | 9 | 9 | 12.5
10 | 13.7 | 24.6 |  | 45 deg elbow | 0.5 | 0.5 | 1 | 1 | 1.5 | 2 | 2.5 | 3.5 | 3.5 | 5
11 | 14.6 | 27 |  | Tee, branch | 2 | 2 | 4.5 | 5.5 | 7 | 9 | 12 | 15 | 14 | 21
12 | 15.4 | 27.8 |  | Tee, run |  |  | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1
13 | 16 | 28.6 |  | Coupling |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1
14 | 16.5 | 29.4 |  | Ball Valve |  |  | 0.5 | 0.5 | 0.5 | 0.5
15 | 17 | 30.2 |  | Gate Valve | [5 empty] | 0.5 | 1 | 1.5 | 2 | 2
16 | 17.5 | 31 |  | Butterfly Valve | [5 empty] | 7.5 | 10 | 15.5 |  | 16
17 | 18 | 31.8 |  | Check Valve | 2.5 | 2.5 | 4.5 | 5.5 | 6.5 | 9 | 11.5 | 14.5 | 12.5 | 18.5
18 | 18.4 | 32.6
19 | 18.8 | 33.4
20 | 19.2 | 34.2
25 | 19.6 | 35
30 | 21.5 | 38
35 | 23.3 | 42
40 | 24.9 | 44
45 | 26.3 | 46
50 | 27.7 | 48
60 | 29.1 | 50
70 | 32 | 54
80 | 35 | 58
90 | 38 | 61.2
100 | 41 | 64.3
120 | 43.5 | 67.5
140 | 48 | 73
160 | 52.5 | 77
180 | 57 | 81
200 | 61 | 85.5
225 | 65 | 90
250 | 70 | 95.5
275 | 75 | 101
300 | 80 | 104.5
400 | 85 | 108
500 | 105 | 127
750 | 124 | 143
1000 | 170 | 177
1250 | 208 | 208
1500 | 239 | 239
1750 | 269 | 269
2000 | 297 | 297
2500 | 325 | 325
3000 | 380 | 380
4000 | 433 | 433
5000 | 525 | 525
5001 | 593 | 593

## Venturi
|  | Point 1 |  |  | Point 2 |  |  | Point 3 |  |  | Point 4 |  |  | Point 5 |  |  | Point 6 |  |  |  |  | Size | ID | Venturi ID | Nozzle ID
| Given | Q = | 37 | GPM | Q = |  | GPM | Q = |  | GPM | Q = |  | GPM | Q = |  | GPM | Q = |  | GPM | Q = | Volumetric flow rate | 1/2" | 0.545
| Values | d = | 1.985 | in | d = | 1.9785 | in | d = | 1.1043 | in | d = | 0.545 | in | d = | 0.545 | in | d = | 1.985 | in | d = | diameter | 3/4" | 0.785
|  | A = |  | sq in | A = |  | sq in | A = |  | sq in | A = |  | sq in | A = |  | sq in | A = |  | sq in | A = | Cross-sectional area | 1" | 1.025
Main size: | 2" | v = |  | ft/sec | v = |  | ft/sec | v = |  | ft/sec | v = |  | ft/sec | v = |  | ft/sec | v = |  | ft/sec | v = | Fluid velocity | 1-1/4" | 1.265 | 1.2313 | 0.70866
Loop size: | 1/2" | P = | 50 | psi | P = |  | psi | P = |  | psi | P = |  | psi | P = |  | psi | P = |  | psi | P = | Pressure | 1-1/2" | 1.505 | 1.4764 | 0.86614
|  | rho = | 1.93 | slug | rho = | 1.93 | slug | rho = | 1.93 | slug | rho = | 1.93 | slug | rho = | 1.93 | slug | rho = | 1.93 | slug | rho = | Density | 2" | 1.985 | 1.9785 | 1.1043
[11 empty] | L = | 24 | ft | L = | 24 | ft
|  | Q = | 37 | GPM | Q = | 34.9631 | GPM | Q = | 34.9631 | GPM | Q = | 2.0369 | GPM | Q = | 2.0369 | GPM | Q = | 37 | GPM
|  | d = | 1.985 | in | d = | 1.9785 | in | d = | 1.1043 | in | d = | 0.545 | in | d = | 0.545 | in | d = | 1.985 | in
|  | A = | 3.0946 | sq in | A = | 3.0745 | sq in | A = | 0.95783 | sq in | A = | 0.23328 | sq in | A = | 0.23328 | sq in | A = | 3.0946 | sq in
|  | v = | 3.8362 | ft/sec | v = | 3.6487 | ft/sec | v = | 11.712 | ft/sec | v = | 2.8016 | ft/sec | v = | 2.8016 | ft/sec | v = | 3.8362 | ft/sec
|  | P = | 50 | psi | P = | 50 | psi | P = | 49.17 | psi | P = | 50 | psi | P = | 49.1698 | psi | P = | 49.17 | psi | Delta P = | -0.00016431
|  | rho = | 1.93 | slug | rho = | 1.93 | slug | rho = | 1.93 | slug | rho = | 1.93 | slug | rho = | 1.93 | slug | rho = | 1.93 | slug
How the sheet works: | [8 empty] | User Input Cells
| Values are entered for pipe sizes, flow, length, etc. | [7 empty] | Calculated Values, Constants
| Using Pascal's law, the pressure at adjacent points is constant. | [7 empty] | Important Values
Points: 1, 2, and 4 are adjacent as are points: 3, 5, and 6
At point 2: P2 = P1, Q2 < Q1, A2 ~ A1
At point 4: P4 = P1, Q4 = (Q1 - Q2), A4 < A1
Due to the conservation of mass, the mass flow rate is constant between 1 and 6, 2 and 3, and 4 and 5
From point 2 to 3, mass flow is constant, density is also constant therefore volumetric flow is constant
Use Bernoulli's equation to find values at point 3 based on values at point 2
(both sides of Bernoulli's are multiplied by rho, to achieve pressure units)
use Hazen-Williams to find P5 based on P4
If P3 < P5, flow through the loop occurs
How to use the sheet:
Enter values in all yellow cells (Q4 should be a small positive number or 0)
Gray cells contain formulas, do not change them
On the "Data" Ribbon, click "What-If-Analysis", on the drop-down, click "Goal Seek"
In the pop-up window for goal seek,
Set cell: U15
To value: 0
By changing cell: N11
Water flows along the path of least resistance. This page compares resistance through the Venturi to the resistance through the loop and changes the flow
through the loop until the resistance in both paths are the same.
Note on D8: 1.93 is the density of water at room temperature
Note on L9: L is the total developed length of the loop from 4 to 5

## EquivLength
0.5
This tab contains a stand alone calculator to find equivalent lengths of a combination of fittings. | [6 empty] | 0.75
*The calculator on this tab is not linked to any other portion of the program. | [6 empty] | 1
1 | Select pipe size in upper yellow cell (E10). | [5 empty] | 1.25
2 | Enter quantity of each type of fitting used in yellow cells (D13:D21). | [5 empty] | 1.5
3 | Column E shows the equivalent length of each type of fitting. | [5 empty] | 2
4 | Total equivalent length of fittings shown will display in blue at the bottom (F23). | [5 empty] | 2.5
3
|  | pipe size: | 0.5 | in |  |  | 3.5
Fitting Type | [6 empty] | 4
|  | qty. | equiv length (ft)
90 deg elbow |  | 5 | 1 | 5
45 deg elbow |  |  | 0.5 | 0 |  | User Input Cells
Tee, branch |  |  | 2 | 0 |  | Calculated Values, Constants
Tee, run |  |  | 0 | 0 |  | Important Values
Coupling |  |  | 0 | 0
Ball Valve |  |  | 0 | 0
Gate Valve |  |  | 0 | 0
Butterfly Valve |  |  | 0 | 0
Check Valve |  |  | 2.5 | 0
Equivalent length of listed fittings:
|  |  |  | 5 | ft